## 自控设备一览表 LIST OF EQUIPMENT
|  |  | 斯里兰卡GAL-OYA糖厂日榨2500吨新增糖线和联合电站及现有制炼车间扩建项目 SRI LANKA GAL-OYA 2500 TCD NEW MILL TENDEM WITH CO-GENERATION POWER PLANT AND EXPANSION OF EXISTING PROCESS HOUSE PROJECT | [5 empty] | 压榨车间火灾自动报警系统 AUTOMATIC FIRE ALARM SYSTEM FOR MILLING HOUSE |  | 版别 REV | 0 | 图号 DRAWING No.
[11 empty] | 设计专业 SPECIALITY | 自 控 CONTROL | 04Z20230047-SZ(X)14A-B1
工程设计证书 A244064796 CERTIFICATE No. A244064796 |  |  | 自 控 设 备 一 览 表 LIST OF AUTOMATIC EQUIPMENT | [7 empty] | 设计阶段 PHASE | 施工图 DETAIL | 日期 D/M/Y | 2023-11-25
自控设备一览表
LIST OF AUTOMATIC EQUIPMENT
|  |  | 项目名称： |  |  | 斯里兰卡GAL-OYA糖厂日榨2500吨新增糖线和联合电站及现有制炼车间扩建项目 SRI LANKA GAL-OYA 2500 TCD NEW MILL TENDEM WITH CO-GENERATION POWER PLANT AND EXPANSION OF EXISTING PROCESS HOUSE PROJECT
PROJECT NAME
建设单位：
DEVELOPMENT ORGANIZATION
工程号：
PROJECT NO.
|  |  | 设计阶段： |  |  | 施工图 DETAIL
PHASE
3
2
1
0 |  |  | 杜海粼 |  |  |  | 蒋悦孟 |  | 丁宇 |  | 丁宇 |  |  | 彭卫平
版次 Rev. | 说明 DESCRIPTION |  | 制表/日期 DRAWNED/DATE |  |  |  | 校核/日期 CHECKED/DATE |  | 审核/日期 VERIFIED/DATE | 注册师/日期 R.DESIGNER VERIFIED/DATE | 分项/日期 P.LEADER/DATE | 项师/日期 LEAD ENG/DATE |  | 审定/日期 APPROVED/DATE
|  |  | 斯里兰卡GAL-OYA糖厂日榨2500吨新增糖线和联合电站及现有制炼车间扩建项目 SRI LANKA GAL-OYA 2500 TCD NEW MILL TENDEM WITH CO-GENERATION POWER PLANT AND EXPANSION OF EXISTING PROCESS HOUSE PROJECT | [5 empty] | 压榨车间火灾自动报警系统 AUTOMATIC FIRE ALARM SYSTEM FOR MILLING HOUSE |  | 阶 段 PHASE | 施工图 DETAIL | 图号 DRAWING No.
[11 empty] | 日 期 D/M/Y | 2023-11-25 | 04Z20230047-SZ(X)14A-B1
工程设计证书 A244064796 CERTIFICATE No. A244064796 |  |  | 自 控 设 备 一 览 表 LIST OF AUTOMATIC EQUIPMENT | [7 empty] | 版 别 REV. | 0 | 制表 DRAWED | 杜海粼
序号 No. | 仪表位号 Instrument NO. | 用 途 Process Duty | 介质 Medium | [5 empty] | 名 称 Description | 型 号 Unit Type | 安装地点 Installed Position | 安装图号 Dwg. No | 数量 Qty. | 备 注 REMARK
|  |  | 名称 Name | 密度 ㎏/m3 | 温度 ℃ | 表压 Mpa | 液位 Level m | 其他 Else
1 | 一、设备 Devices | 火灾自动报警系统 Automatic fire alarm system | [6 empty] | 接线箱 | 含浪涌保护器、接线端子等，配安装支架及螺栓等安装材料 | FJ14A01 |  | 1 | 单位：个
[9 empty] | Junction box | Including surge protectors, wiring terminals, etc., equipped with installation brackets and bolts and other installation materials | FJ14A01 |  |  | Unit: pieces
2 | [8 empty] | 接线箱 | 含接线端子等，配安装支架及螺栓等安装材料 | FJ14A02~03 |  | 2 | 单位：个
[9 empty] | Junction box | Including wiring terminals, equipped with installation brackets, bolts, and other installation materials | FJ14A02~03 |  |  | Unit: pieces
3 | [8 empty] | 模块箱 | 含接线端子等，配安装支架及螺栓等安装材料 | MB14A01 |  | 1 | 单位：个
[9 empty] | Module box | Including wiring terminals, equipped with installation brackets, bolts, and other installation materials | MB14A01 |  |  | Unit: pieces
4 | [8 empty] | 信号总线浪涌保护器 | SPD，类别：D1； 试验类型：高能量； 开路电压：≥1kV； 短路电流：1.5kA，10/350μs |  |  | 1 | 接线箱内设备 单位：对
[9 empty] | Signal bus surge protector | SPD, category: D1; Test type: High energy; Open circuit voltage: ≥ 1kV; Short circuit current: 1.5kA, 10/350 μ S |  |  |  | Equipment inside the junction box Unit: pairs
5 | [8 empty] | 电源总线浪涌保护器 | SPD，类别：D1； 试验类型：高能量； 开路电压：≥1kV； 短路电流：1.5kA，10/350μs |  |  | 1 | 接线箱内设备 单位：对
[9 empty] | Power bus surge protector | SPD, category: D1; Test type: High energy; Open circuit voltage: ≥ 1kV; Short circuit current: 1.5kA, 10/350 μ S |  |  |  | Equipment inside the junction box Unit: pairs
6 | [8 empty] | 广播总线浪涌保护器 | SPD，类别：D1； 试验类型：高能量； 开路电压：≥1kV； 短路电流：1.5kA，10/350μs |  |  | 1 | 接线箱内设备 单位：对
[9 empty] | Broadcast bus surge protector | SPD, category: D1; Test type: High energy; Open circuit voltage: ≥ 1kV; Short circuit current: 1.5kA, 10/350 μ S |  |  |  | Equipment inside the junction box Unit: pairs
7 | [8 empty] | 电话总线浪涌保护器 | SPD，类别：D1； 试验类型：高能量； 开路电压：≥1kV； 短路电流：1.5kA，10/350μs |  |  | 1 | 接线箱内设备 单位：对
[9 empty] | Telephone bus surge protector | SPD, category: D1; Test type: High energy; Open circuit voltage: ≥ 1kV; Short circuit current: 1.5kA, 10/350 μ S |  |  |  | Equipment inside the junction box Unit: pairs
8 | [8 empty] | 感烟火灾探测器（点型） | 编码型；配接线盒、安装底座 |  |  | 16 | 单位：个
[9 empty] | Smoke and fire detector (point type) | Encoding type; Equipped with junction box and installation base |  |  |  | Unit: pieces
9 | [8 empty] | 缆式线型感温火灾探测器 | 模拟量加开关量，感温电缆可恢复，长度不小于20m，配转换盒、终端盒 | ±0.000m电缆夹层 |  | 3 | 单位：套
[9 empty] | Cable type linear thermal fire detector | Analog quantity plus switch quantity, temperature sensing cable recoverable, length not less than 20m, equipped with conversion box and terminal box | ± 0.000m cable interlayer |  |  | Unit: Sets
10 | [8 empty] | 感温火灾探测器（点型、防爆型） | 编码型；配接线盒、安装底座 防爆等级：ExdIICT4 |  |  | 6 | 单位：个
[9 empty] | Temperature sensitive fire detectors (point type, explosion-proof type) | Encoding type; Equipped with junction box and installation base Explosion proof level: ExdIICT4 |  |  |  | Unit: pieces
11 | [8 empty] | 带火警电话插孔的手动报警按钮 | 编码型；配接线盒、安装底座 |  |  | 10 | 单位：个
[9 empty] | Manual alarm button with fire alarm telephone jack | Encoding type; Equipped with junction box and installation base |  |  |  | Unit: pieces
12 | [8 empty] | 手动报警按钮（防爆型） | 编码型；配接线盒、安装底座 防爆等级：ExdIICT4 |  |  | 1 | 单位：个
[9 empty] | Manual alarm button (explosion-proof type) | Encoding type; Equipped with junction box and installation base Explosion proof level: ExdIICT4 |  |  |  | Unit: pieces
13 | [8 empty] | 火灾声光警报器 | 编码型；配接线盒、安装底座 |  |  | 10 | 单位：个
[9 empty] | Fire sound and light alarm | Encoding type; Equipped with junction box and installation base |  |  |  | Unit: pieces
14 | [8 empty] | 火灾声光警报器（防爆型） | 编码型；配接线盒、安装底座 防爆等级：ExdIICT4 |  |  | 1 | 单位：个
[9 empty] | Fire sound and light alarm (explosion-proof type) | Encoding type; Equipped with junction box and installation base Explosion proof level: ExdIICT4 |  |  |  | Unit: pieces
15 | [8 empty] | 火灾应急广播扬声器（壁挂式） |  |  |  | 11 | 单位：个
[9 empty] | Fire emergency broadcasting speaker (wall mounted) |  |  |  |  | Unit: pieces
16 | [8 empty] | 火灾应急广播扬声器（壁挂式、防爆型） | 防爆等级：ExdIICT4 |  |  | 1 | 单位：个
[9 empty] | Fire emergency broadcasting speaker (wall mounted, explosion-proof) | Explosion proof level: ExdIICT4 |  |  |  | Unit: pieces
17 | [8 empty] | 火警电话分机 |  |  |  | 3 | 单位：个
[9 empty] | Fire alarm telephone extension |  |  |  |  | Unit: pieces
18 | [8 empty] | 火警电话分机（防爆型） | 防爆等级：ExdIICT4 |  |  | 1 | 单位：个
[9 empty] | Fire alarm telephone extension (explosion-proof type) | Explosion proof level: ExdIICT4 |  |  |  | Unit: pieces
19 | [8 empty] | 总线隔离模块 | 可隔离电源及信号总线，树状分支结构系统设备 |  |  | 3 | 单位：个
[9 empty] | Bus isolation module | Isolatable power and signal bus, tree branch structure system equipment |  |  |  | Unit: pieces
20 | [8 empty] | 总线广播模块 |  |  |  | 3 | 单位：个
[9 empty] | Bus broadcast module |  |  |  |  | Unit: pieces
21 | [8 empty] | 总线电话模块 |  |  |  | 7 | 单位：个
[9 empty] | Bus telephone module |  |  |  |  | Unit: pieces
22 | [8 empty] | 输入模块 |  |  |  | 6 | 单位：个
[9 empty] | Input module |  |  |  |  | Unit: pieces
23 | [8 empty] | 输入/输出模块 |  |  |  | 5 | 单位：个
[9 empty] | I/O module |  |  |  |  | Unit: pieces
24 |  | 可燃气体探测报警系统 | [6 empty] | 可燃气体报警控制器 |  | 油箱间外 |  | 1 | 单位：个
|  | Combustible gas detection and alarm system | [6 empty] | Combustible gas alarm controller |  | Outside the fuel tank room |  |  | Unit: pieces
25 | [8 empty] | 可燃气体探测器（防爆型，自带声光报警） | 探测气体：轻柴油、烃类混合物气体 | 油箱间 |  | 2 | 单位：个
[9 empty] | Combustible gas detector (explosion-proof type, with built-in sound and light alarm) | Detection gas: light diesel, hydrocarbon mixture gas | Fuel tank room |  |  | Unit: pieces
26 | 二、材料 Materials | [7 empty] | 火灾报警信号总线 Fire alarm signal line | ZCN-RVS-300/500V-2x1.5mm2 | 室内 Indoor |  | 310 | 单位：米 Unit: meters
27 | [9 empty] | ZCN-KVVSP22-450/750V-4x1.5mm2 | 室外 Outdoor |  | 105 | 单位：米 Unit: meters
28 | [8 empty] | 消防专用电话总线 Firefighting dedicated telephone line | ZCN-RVS-300/500V-2x1.5mm2 | 室内 Indoor |  | 220 | 单位：米 Unit: meters
29 | [9 empty] | ZCN-KVVSP22-450/750V-4x1.5mm2 | 室外 Outdoor |  | 105 | 单位：米 Unit: meters
30 | [8 empty] | 消防应急广播总线 Fire emergency broadcasting line | ZCN-RVS-300/500V-2x1.5mm2 | 室内 Indoor |  | 220 | 单位：米 Unit: meters
31 | [9 empty] | ZCN-KVVSP22-450/750V-4x1.5mm2 | 室外 Outdoor |  | 105 | 单位：米 Unit: meters
32 | [8 empty] | DC24V电源线 DC24V power line | ZCN-BV-450/750V-2(1x2.5mm2) | 室内 Indoor |  | 310 | 单位：米 Unit: meters
33 | [9 empty] | ZCN-YJV22-450/750V-3x4.0mm2 | 室外 Outdoor |  | 105 | 单位：米 Unit: meters
34 | [8 empty] | 镀锌钢管 Galvanized steel pipe | DN20，GB/T 3091-2015 | 室内 Indoor |  | 750 | 单位：米 Unit: meters
35 | [9 empty] | DN50，GB/T 3091-2015 | 室外 Outdoor |  | 5 | 单位：米 Unit: meters
36 | [8 empty] | 管卡子 | 适配镀锌钢管DN20 |  |  | 400 | 单位：个
[9 empty] | pipe clamp | Adapted to galvanized steel pipe DN20 |  |  |  | Unit: pieces
37 | [8 empty] | 电线管直通接头（内螺纹） | 适配镀锌钢管DN20 |  |  | 180 | 单位：个
[9 empty] | Wire conduit straight connector (internal thread) | Wire conduit straight connector (internal thread) |  |  |  | Unit: pieces
38 | [8 empty] | 钢制明装过线盒（带敲落孔） | 适配镀锌钢管DN20 |  |  | 80 | 单位：个
[9 empty] | Steel surface mounted wire box (with tapping holes) | Wire conduit straight connector (internal thread) |  |  |  | Unit: pieces
39 | [8 empty] | 锁紧螺母 | DN20 |  |  | 180 | 单位：个
[9 empty] | Locking nut | DN20 |  |  |  | Unit: pieces
erty