## 自控设备一览表 LIST OF EQUIPMENT
|  |  | 斯里兰卡GAL-OYA糖厂日榨2500吨新增糖线和联合电站及现有制炼车间扩建项目 SRI LANKA GAL-OYA 2500 TCD NEW MILL TENDEM WITH CO-GENERATION POWER PLANT AND EXPANSION OF EXISTING PROCESS HOUSE PROJECT | [5 empty] | 锅炉间、动力间火灾自动报警系统 AUTOMATIC FIRE ALARM SYSTEM FOR BOILER HOUSE AND POWER HOUSE |  | 版别 REV | 0 | 图号 DRAWING No.
[11 empty] | 设计专业 SPECIALITY | 自 控 CONTROL | 04Z20230047-SZ(X)41,46-B1
工程设计证书 A244064796 CERTIFICATE No. A244064796 |  |  | 自 控 设 备 一 览 表 LIST OF AUTOMATIC EQUIPMENT | [7 empty] | 设计阶段 PHASE | 施工图 DETAIL | 日期 D/M/Y | 2023-11-25
自控设备一览表
LIST OF AUTOMATIC EQUIPMENT
|  |  | 项目名称： |  |  | 斯里兰卡GAL-OYA糖厂日榨2500吨新增糖线和联合电站及现有制炼车间扩建项目 SRI LANKA GAL-OYA 2500 TCD NEW MILL TENDEM WITH CO-GENERATION POWER PLANT AND EXPANSION OF EXISTING PROCESS HOUSE PROJECT
PROJECT NAME
建设单位：
DEVELOPMENT ORGANIZATION
工程号：
PROJECT NO.
|  |  | 设计阶段： |  |  | 施工图 DETAIL
PHASE
3
2
1
0 |  |  | 杜海粼 |  |  |  | 蒋悦孟 |  | 丁宇 |  | 丁宇 |  |  | 彭卫平
版次 Rev. | 说明 DESCRIPTION |  | 制表/日期 DRAWNED/DATE |  |  |  | 校核/日期 CHECKED/DATE |  | 审核/日期 VERIFIED/DATE | 注册师/日期 R.DESIGNER VERIFIED/DATE | 分项/日期 P.LEADER/DATE | 项师/日期 LEAD ENG/DATE |  | 审定/日期 APPROVED/DATE
|  |  | 斯里兰卡GAL-OYA糖厂日榨2500吨新增糖线和联合电站及现有制炼车间扩建项目 SRI LANKA GAL-OYA 2500 TCD NEW MILL TENDEM WITH CO-GENERATION POWER PLANT AND EXPANSION OF EXISTING PROCESS HOUSE PROJECT | [5 empty] | 锅炉间、动力间火灾自动报警系统 AUTOMATIC FIRE ALARM SYSTEM FOR BOILER HOUSE AND POWER HOUSE |  | 阶 段 PHASE | 施工图 DETAIL | 图号 DRAWING No.
[11 empty] | 日 期 D/M/Y | 2023-11-25 | 04Z20230047-SZ(X)41,46-B1
工程设计证书 A244064796 CERTIFICATE No. A244064796 |  |  | 自 控 设 备 一 览 表 LIST OF AUTOMATIC EQUIPMENT | [7 empty] | 版 别 REV. | 0 | 制表 DRAWED | 杜海粼
序号 No. | 仪表位号 Instrument NO. | 用 途 Process Duty | 介质 Medium | [5 empty] | 名 称 Description | 型 号 Unit Type | 安装地点 Installed Position | 安装图号 Dwg. No | 数量 Qty. | 备 注 REMARK
|  |  | 名称 Name | 密度 ㎏/m3 | 温度 ℃ | 表压 Mpa | 液位 Level m | 其他 Else
1 | 一、设备 Devices | 火灾自动报警系统 Automatic fire alarm system | [6 empty] | 接线箱 | 含浪涌保护器、接线端子等，配安装支架及螺栓等安装材料 | FJ4101 |  | 1 | 单位：个
[9 empty] | Junction box | Including surge protectors, wiring terminals, etc., equipped with installation brackets and bolts and other installation materials | FJ4101 |  |  | Unit: pieces
2 | [8 empty] | 接线箱 | 含接线端子等，配安装支架及螺栓等安装材料 | FJ4102~06 |  | 5 | 单位：个
[9 empty] | Junction box | Including wiring terminals, equipped with installation brackets, bolts, and other installation materials | FJ4102~06 |  |  | Unit: pieces
3 | [8 empty] | 模块箱 | 含接线端子等，配安装支架及螺栓等安装材料 | MB4101~04 |  | 4 | 单位：个
[9 empty] | Module box | Including wiring terminals, equipped with installation brackets, bolts, and other installation materials | MB4101~04 |  |  | Unit: pieces
4 | [8 empty] | 信号总线浪涌保护器 | SPD，类别：D1； 试验类型：高能量； 开路电压：≥1kV； 短路电流：1.5kA，10/350μs |  |  | 5 | 接线箱内设备 单位：对
[9 empty] | Signal bus surge protector | SPD, category: D1; Test type: High energy; Open circuit voltage: ≥ 1kV; Short circuit current: 1.5kA, 10/350 μ S |  |  |  | Equipment inside the junction box Unit: pairs
5 | [8 empty] | 感烟火灾探测器（点型） | 编码型；配接线盒、安装底座 |  |  | 19 | 单位：个
[9 empty] | Smoke and fire detector (point type) | Encoding type; Equipped with junction box and installation base |  |  |  | Unit: pieces
6 | [8 empty] | 缆式线型感温火灾探测器 | 模拟量加开关量，感温电缆可恢复，长度不小于65m，配转换盒、终端盒 | 4.500m电缆夹层 |  | 3 | 单位：套
[9 empty] | Cable type linear thermal fire detector | Analog quantity plus switch quantity, temperature sensing cable recoverable, length not less than 65m, equipped with conversion box and terminal box | 4.500m cable interlayer |  |  | Unit: Sets
7 | [8 empty] | 缆式线型感温火灾探测器 | 模拟量加开关量，感温电缆可恢复，长度不小于30m，配转换盒、终端盒 | 11.500m设备平台 |  | 2 | 单位：套
[9 empty] | Cable type linear thermal fire detector | Analog quantity plus switch quantity, temperature sensing cable recoverable, length not less than 30m, equipped with conversion box and terminal box | 11.500m device platform |  |  | Unit: Sets
8 | [8 empty] | 缆式线型感温火灾探测器 | 模拟量加开关量，感温电缆可恢复，长度不小于25m，配转换盒、终端盒 | 23.500m设备平台 |  | 2 | 单位：套
[9 empty] | Cable type linear thermal fire detector | Analog quantity plus switch quantity, temperature sensing cable recoverable, length not less than 25m, equipped with conversion box and terminal box | 23.500m device platform |  |  | Unit: Sets
9 | [8 empty] | 带火警电话插孔的手动报警按钮 | 编码型；配接线盒、安装底座 |  |  | 13 | 单位：个
[9 empty] | Manual alarm button with fire alarm telephone jack | Encoding type; Equipped with junction box and installation base |  |  |  | Unit: pieces
10 | [8 empty] | 消火栓破玻按钮 | 编码型；配接线盒、安装底座 |  |  | 27 | 单位：个
[9 empty] | Fire hydrant glass breaking button | Encoding type; Equipped with junction box and installation base |  |  |  | Unit: pieces
11 | [8 empty] | 火灾声光警报器 | 编码型；配接线盒、安装底座 |  |  | 27 | 单位：个
[9 empty] | Fire sound and light alarm | Encoding type; Equipped with junction box and installation base |  |  |  | Unit: pieces
12 | [8 empty] | 火灾应急广播扬声器（壁挂式） |  |  |  | 16 | 单位：个
[9 empty] | Fire emergency broadcasting speaker (wall mounted) |  |  |  |  | Unit: pieces
13 | [8 empty] | 火灾应急广播扬声器（吸顶式） |  |  |  | 4 | 单位：个
[9 empty] | Fire emergency broadcasting speaker (ceiling mounted) |  |  |  |  | Unit: pieces
14 | [8 empty] | 火警电话分机 |  |  |  | 5 | 单位：个
[9 empty] | Fire alarm telephone extension |  |  |  |  | Unit: pieces
15 | [8 empty] | 总线隔离模块 | 可隔离电源及信号总线，树状分支结构系统设备 |  |  | 9 | 单位：个
[9 empty] | Bus isolation module | Isolatable power and signal bus, tree branch structure system equipment |  |  |  | Unit: pieces
16 | [8 empty] | 总线广播模块 |  |  |  | 5 | 单位：个
[9 empty] | Bus broadcast module |  |  |  |  | Unit: pieces
17 | [8 empty] | 总线电话模块 |  |  |  | 11 | 单位：个
[9 empty] | Bus telephone module |  |  |  |  | Unit: pieces
18 | [8 empty] | 输入模块 |  |  |  | 27 | 单位：个
[9 empty] | Input module |  |  |  |  | Unit: pieces
19 | [8 empty] | 输入/输出模块 |  |  |  | 17 | 单位：个
[9 empty] | I/O module |  |  |  |  | Unit: pieces
20 |  | 消防水箱液位监测系统 Fire water tank liquid level monitoring system | [6 empty] | 带远传磁翻板液位计 | 两线制，4~20mA信号输出，电气接口：M20内螺纹，精度：±10mm，接液及浮子材质：304不锈钢，侧装方式，法兰连接，法兰中心距：650mm，DN25 PN1.0MPa法兰过程连接，配供不锈钢安装法兰、螺栓、螺母、垫片，防护等级IP65，配供DN25 PN1.0MPa不锈钢法兰式闸阀 |  |  | 1 | 单位：个
[9 empty] | Equipped with remote magnetic flap level gauge | Two wire system, 4-20mA signal output, electrical interface: M20 internal thread, accuracy: ± 10mm, liquid connection and float material: 304 stainless steel, side installation method, flange connection, flange center distance: 650mm, DN25 PN1.0MPa flange process connection, equipped with stainless steel installation flange, bolts, nuts, washers, protection level IP65, equipped with DN25 PN1.0MPa stainless steel flange gate valve |  |  |  | Unit: pieces
21 | [8 empty] | 靶式流量开关 | 插入式，两副常开触点，动作流量：3L/s，管道直径：DN25，配安装材料 |  |  | 1 | 单位：套
[9 empty] | Target flow switch | Insertion type, two pairs of normally open contacts, operating flow rate: 3L/s, pipeline diameter: DN25, equipped with installation materials |  |  |  | Unit: sets
22 |  | 消防控制室设备 Fire control room equipment | [6 empty] | 火灾自动报警系统主机柜 | 带直流蓄电池、联动控制盘、消防电话系统、消防广播系统、手动控制盘等 |  |  | 1 | 单位：套
[9 empty] | Main cabinet of fire automatic alarm system | Equipped with DC battery, linkage control panel, fire telephone system, fire broadcasting system, manual control panel, etc |  |  |  | Unit: sets
23 | [8 empty] | 控制室图形显示装置 | 正版系统操作软件、带操作台 |  |  | 1 | 单位：套
[9 empty] | Control room graphic display device | Genuine system operating software with console |  |  |  | Unit: sets
24 | [8 empty] | 应急照明控制主机 | 工作电压：AC240V |  |  | 1 | 单位：套 电气专业设备
[9 empty] | Emergency lighting control host | Working voltage: AC240V |  |  |  | Unit: Sets Electrical professional equipment
25 | [8 empty] | 液位显示箱 | 600x300x600（WxDxH）（暂定，可由设备商根据实际需求调整），下进下出 |  |  | 1 | 单位：套 内部配置详见液位显示箱电气原理图
[9 empty] | Liquid level display box | 600x300x600 (WxDxH) (tentative, can be adjusted by the equipment supplier according to actual needs), bottom in and bottom out |  |  |  | Unit: Sets Please refer to the electrical schematic of the liquid level display box for internal configuration details
26 | [8 empty] | 消防控制室设备配电箱 | 按系统图配置 |  |  | 1 | 单位：套
[9 empty] | Fire control room equipment distribution box | Configure according to system diagram |  |  |  | Unit: sets
27 | 二、材料 Materials | [7 empty] | 火灾报警信号总线 Fire alarm signal line | ZCN-RVS-300/500V-2x1.5mm2 | 室内 Indoor |  | 720 | 单位：米 Unit: meters
28 | [8 empty] | 消防专用电话总线 Firefighting dedicated telephone line | ZCN-RVS-300/500V-2x1.5mm2 | 室内 Indoor |  | 520 | 单位：米 Unit: meters
29 | [8 empty] | 消防应急广播总线 Fire emergency broadcasting line | ZCN-RVS-300/500V-2x1.5mm2 | 室内 Indoor |  | 520 | 单位：米 Unit: meters
30 | [8 empty] | DC24V电源线 DC24V power line | ZCN-BV-450/750V-2(1x2.5mm2) | 室内 Indoor |  | 720 | 单位：米 Unit: meters
31 | [8 empty] | 流量开关、压力开关控制线 Flow switch, pressure switch control line | ZCN-KVVP-450/750V-3x1.5mm2 | 室内 Indoor |  | 135 | 单位：米 Unit: meters
32 | [9 empty] | ZCN-KVVP22-450/750V-4x1.5mm2 | 室外 Outdoor |  | 930 | 单位：米 Unit: meters
31 | [8 empty] | 电磁阀控制线 Electromagnetic valve control line | ZCN-KVVP-450/750V-4x1.5mm2 | 室内 Indoor |  | 30 | 单位：米 Unit: meters
34 | [8 empty] | 液位计信号线 Liquid level gauge signal line | ZCN-KVVP-450/750V-4x1.5mm2 | 室内 Indoor |  | 45 | 单位：米 Unit: meters
35 | [8 empty] | 镀锌钢管 Galvanized steel pipe | DN20，GB/T 3091-2015 | 室内 Indoor |  | 1760 | 单位：米 Unit: meters
36 | [9 empty] | DN50，GB/T 3091-2015 | 室外 Outdoor |  | 10 | 单位：米 Unit: meters
37 | [9 empty] | DN100，GB/T 3091-2015 | 室外 Outdoor |  | 5 | 单位：米 Unit: meters
38 | [8 empty] | 防火金属桥架 Fireproof metal cable tray | 150x75，带隔板、盖板，配安装材料 | 室内 |  | 60 | 单位：米
[10 empty] | 150x75, with partition and cover plate, equipped with installation materials | Indoor |  |  | Unit: meters
39 | [9 empty] | 300x100，带隔板、盖板，配安装材料 | 室内 |  | 20 | 单位：米
[10 empty] | 300x100, with partition and cover plate, equipped with installation materials | Indoor |  |  | Unit: meters
40 | [8 empty] | 管卡子 | 适配镀锌钢管DN20 |  |  | 900 | 单位：个
[9 empty] | pipe clamp | Adapted to galvanized steel pipe DN20 |  |  |  | Unit: pieces
41 | [8 empty] | 电线管直通接头（内螺纹） | 适配镀锌钢管DN20 |  |  | 380 | 单位：个
[9 empty] | Wire conduit straight connector (internal thread) | Adapted to galvanized steel pipe DN20 |  |  |  | Unit: pieces
42 | [8 empty] | 钢制明装过线盒（带敲落孔） | 适配镀锌钢管DN20 |  |  | 150 | 单位：个
[9 empty] | Steel surface mounted wire box (with tapping holes) | Adapted to galvanized steel pipe DN20 |  |  |  | Unit: pieces
43 | [8 empty] | 锁紧螺母 | DN20 |  |  | 380 | 单位：个
[9 empty] | locking nut | DN20 |  |  |  | Unit: pieces
44 | [8 empty] | 热镀锌自攻螺丝 | Ф4×30 |  |  | 200 | 单位：个
[9 empty] | Hot dip galvanized self tapping screws | Ф4×30 |  |  |  | Unit: pieces
45 | [8 empty] | 角钢 | L40x40x4 |  |  | 60 | 单位：米
[9 empty] | Angle steel | L40x40x4 |  |  |  | Unit: meters
46 | [8 empty] | 膨胀螺栓 | M8，L＝50，配螺母和垫片 |  |  | 200 | 单位：套
[9 empty] | Expansion bolt | M8, L=50, with nuts and washers |  |  |  | Unit: sets
erty